## Sheet1
OFF GRID PHOTOVOLTAIC POWER SYSTEM SIZING TOOL , v 2.3
This is a free tool provided with absolutely no warranty of suitability for any purposes at all.
This tool is not meant to replace expert professional advice. It can not take into account all variables.
Equipment such as charge controllers and inverters must be matched to the balance of the system.
NOTE: The blue shaded cells are the only cells where you can change or enter values.
This is to protect other cells that may have formulas in them.
There are values entered in some of the cells to serve as an example. Please remove or change them to suit your use.
A period of a week is used to determine the loads as there may be some appliances that are only used once or twice a week.
That weekly number will be averaged to a daily value later down the page.
Part 1, Step A: AC LOADS. If none go to next step "DC LOADS" loads.
List all your AC loads by watts and hours per week of use. If you know the volts and amps, multiply them to get watts.
The chart will multiply the quantity by the watts, by the hours per week and then total them.
Description of AC Loads Run from Inverter |  |  |  | Quantity | Watts | X | Hrs/Wk | = | Watt-Hrs/Week
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
[8 empty] | AC Total Watt-Hours/Week | 0
The default value for inverter efficiency is set to 90%. (using decimal format we have 0.90)
Your inverter may be worse or perhaps better, therefore you can adjust the efficiency factor.
Remember, an inverter used for small loads is less efficient than when being used under higher loads.
0 | divided by | 0.9 | = | 0 | Adjusted WH per Week, AC Loads |  |  |  |  | 0 | Watt-hours (rounded value)
Insert the Inverter input voltage, usually 12 or 24. | [5 empty] | 0 | (known as the DC system voltage)
We divide the Rounded Adjusteded Watt-Hours per week by the inverter input voltage to obtain the Amp Hours per week used for the AC Loads.
0 | divided by | 0 | = | #DIV/0! | Amp-Hours per week used by AC loads
Part 1, Step B: DC LOADS.
List all your DC loads by watts and hours per week of use.
The chart will multiply watts X hrs/Wk and then total them.
Description of DC Loads |  |  |  | Quantity | Watts | X | Hrs/Wk | = | Watt-Hrs/Week
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
|  |  |  | 1 | 0 | X | 0 | = | 0
[8 empty] | DC Total Watt-Hours/Week | 0
DC system voltage (same value used for Inverter input voltage. | [5 empty] | 0 | volts
We divide the DC Watt-Hours per week by the system voltage to determine the Amp-Hours per week used by the DC loads.
0 | divided by | 0 | = | #DIV/0! | Amp-Hours per week used by DC loads
We then add the AC and the DC Amp-Hours used per week, to determine the Total Amp=Hours per week.
#DIV/0! | + | #DIV/0! | = | #DIV/0! | Total Amp-Hours per week
We will now divide the Weekly total Amp-Hours by 7 to determine the Total Daily Amp-Hours used.
#DIV/0! | divided by | 7 | = | #DIV/0! | Total Daily Amp-Hours used
Part 2, Battery Sizing
Point to remember: connecting batteries in series, positive to negative adds the voltages and does not change the Amp-Hours
Connecting batteries in parallel, all negatives together and all positives together, adds the Amp-Hours but does not change the voltage.
A battery bank may have batteries in series strings with those connected in parallel to increase capacity.
A battery bank with the fewest number of cells (or batteries) is preferred to one with many batteries in parallel connection.
Total Daily Amp-Hours used: auto filled from the section above... |  |  |  |  | #DIV/0! | Total Daily Amp-Hours used
How many autonomous power days of use would you like? (Cloudy, no sun or low solar energy days)
Two days may be ample in areas with predominantly sunny days, others may need more.
Insert the number of days of autonomy desired.... |  |  |  |  | 0 | days
We multiply the Amp-Hour requirement by the number of days.
| #DIV/0! | X | 0 | = | #DIV/0! | Autonomous Amp-Hours Capacity required
Choose the depth of discharge for the battery. A value of 0.2 means we will use only 20% of the capacity of the battery.
Many people will use a maximum depth of discharge of 50%, a value is 0.5
You should never discharge more than 80%, a value of 0.8 |  |  |  |  | 0 | Depth of discharge limit
We divide the Autonomous Amp-Hours Capacity required by the Depth of Discharge limit
| #DIV/0! | divided by | 0 | = | #DIV/0! | Amp-Hours Capacity
Battery capacity is reduced as temperatures fall below 77 degrees F.
From the chart below select the factor that corresponds to the average coldest temperature the batteries will be subjected to
[5 empty] | 1.18 | Temperature factor
80 F | 1 |  | 40 F | 1.18 |  |  | 0F |  | 1.42
70 F | 1.04 |  | 30 F | 1.22 |  |  | -10F |  | 1.48
60 F | 1.08 |  | 20F | 1.28 |  |  | -20F |  | 1.55
50 F | 1.12 |  | 10F | 1.33
We multiply the Amp-Hours Capacity by the temperature factor to obtain the total battery capacity required.
| #DIV/0! | X | 1.18 | = | #DIV/0! | Total Amp-Hour Capacity for the battery
Find a battery you might use. Enter the battery model for your records
Enter the volts and the Amp-Hour capacity of the battery
Trojan L16RE-B |  |  | 6 | volts | 370 | Amp-Hours rating
(Remember, this is only an example, replace the sample data with your selection)
We divide the Total Amp-Hour Capacity for the battery by the battery Amp-Hours rating
This is the number of batteries wired in parallel required.
| #DIV/0! | divided by | 370 | = | #DIV/0! | batteries
We round this result up to the next highest number. |  |  |  |  | #DIV/0! | (rounded up value) |  |  |  | #DIV/0! | (rounded down)
If you do not want to round the value up use the rounded down value in the yellow shaded cell.
Rounding down will reduce your battery capacity and may lead to unsatisfactory system performance.
We divide the system voltage by the individual battery voltage.
This is the number of batteries wired in series that is required.
| 0 | divided by | 6 | = | 0
We multiply the number of batteries in parallel by the number of batteries in series.
This is the total number of batteries required,
| #DIV/0! | X | 0 | = | #DIV/0! | =Total batteries required |  |  |  | #DIV/0! | (= less capacity)
Part 3: PV Array Sizing
The maximum power voltage (Vmp) of the panel should be about 1.5 times that of the voltage of the battery / battery bank.
That is, a 12 volt battery should have panels with a Vmp of around 18 volts; a 24 volt battery should have a panel Vmp of about 36 volts.
Some charge controllers can accept much higher voltage inputs and step the output doen to the required battery voltage.
That can allow panels to be connected in series which can save on costs of wire over long runs.
For simplicity we'll first assume that the panel Vmp's are a proper match for the battery bank. (approx. 18 Vmp for a 12 volt battery....)
That means we will assume the panels will be connected in parallel, all negatives together and all positives together.
Total Daily average Amp-Hours per day from load sizing.. |  |  |  |  | #DIV/0!
Batteries are not 100% efficient in charging and discharging.
We will add 20% to compensate for that inefficiency.
| #DIV/0! | X | 1.2 | = | #DIV/0!
Enter the average number of sun hours for your area. |  |  |  |  | 0
Refer to the maps in the topic or use the maps available at... http://www.nrel.gov/gis/solar.html
Scroll down to “PV Solar Radiation (Flat Plate, Facing South, Latitude Tilt)—Static Maps”
We divide the Amp-Hours by the sun hours.
| #DIV/0! | divided by | 0 | = | #DIV/0! | Total Amps required from Solar array
Select a PV panel candidate. Look up the output data
Kyocera KC130, 17.6 Vmp, 7.39 Imp,
Enter the Imp (maximum power amps) |  |  |  |  | 7.39 | Imp (Maximum power Amps)
(Remember, this is only an example, replace the sample data with your selection)
Divide the Total Amps from Solar Array required by the Imp value
| #DIV/0! | divided by | 7.39 | = | #DIV/0!
We round this result up to the next highest number. |  |  |  |  | #DIV/0!
Determine how many panels are required in series to produce correct voltage for panel charging.
(panels should have Vmp of approx 18 volts for a 12 volt system; 36 volts for 24 volts systems)
Enter the number of panels in series required |  |  |  |  | 1 | panels in series
(You have to think a little there.)
Multiply the number of panels in parallel by the number is series
| #DIV/0! | X | 1 | = | #DIV/0! | Total number of PV panels required.
The charge controller selected must be able to handle the current and the voltages that may be generated by the PV panels.
The output voltages of PV panels increases with cold temperatures and must be considered when selecting equipment.
The output amperage of PV panels may increase at higher altitudes and must be considered when selecting equipment.